## SETUP
WAF Calculation Spreadsheet for "Test Method - Determination of Volumetric Gas Flow in Rectangular Ducts or Stacks Tacking into Account Velocity Decay near the Stack or Duct Walls
Developed for EPRI by Stephen K. Norfleet, RMB Consulting & Research, Inc. (919) 791-3123
Method 1 Test Matrix: |  |  |  | Value |  | Comments:
Test Ports |  |  |  | 4 |  | Number of Method 1 Test Ports
Points per Port |  |  |  | 4 |  | Number of Method 1 traverse points measured from each port (including any Method 1 traverse points that may be measured from ports on oposite wall)
Duct/Stack Dimensions: |  |  |  | Value
Duct/Stack Width (ft) |  |  |  | 12 |  | Interior length of test port wall from adjacent wall to adjacent wall at testing cross-section (Ly)
Duct/Stack Depth (ft) |  |  |  | 18.5 |  | Interior distance from test port wall to the opposite stack/duct wall at testing cross-section (Lx)
Wall Effects Test Details: |  |  |  | Value
WAF Calculation Approach (M, L, or D) |  |  |  | M |  | Enter "M" for full measurement-based, "L" for logarithmic/overlay assisted (Section 8.5.1 of Test Method), or "D" for duct or stack specific default (Section 8.5.2 of Test Method) | [10 empty] | M
One-Inch Intervals |  |  |  | 12 |  | Number of near wall one-inch intervals (number of points starting with 1" regardless of whether 1" is the first available point)
Extra Non-Method 1 Ports |  |  |  | 0 |  | Number of extra, non-Method 1 alternative ports where wall effects traverses were performed
Ash Correction Required? (Y or N) |  |  |  | N |  | Enter "Y" only if an ash layer is present and the Method 1 test ports are located on a vertical wall on a horizontal or included duct and the test port placement does not take into consideration the ash layer | [10 empty] | N
Ash Depth, If Ash Correction Required (in) |  |  |  | 0 |  | If required, ash depth in duct at test location
Port Specific Information: |  |  |  | A | B | C | D
First Available One-inch Interval |  |  |  | 1 | 1 | 1 | 1 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Include Port in WAF Calc.? (Y or N) |  |  |  | Y | Y | Y | Y | [9 empty] | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
Spreadsheet Layout: |  |  |  | Option
Traverse Point Order (A, D or G) |  |  |  | A |  | Order of traverse points on "Data" sheet (A = Ascending, D = Descending, G= Group by Type) | [10 empty] | A
Setup Data Points
| Dbx | 55.5 | Dby | 36 | Intervalx | 12 | Intervaly | 12 | TIntervals | 12
| dM1y | 18 | Dremx | 33.75 | dremy | 24 | dM1ash |  | dremash
| Traverse Points |  | Measurement-based |  | Log/Overlap Assist |  | Other Points
| Method 1 |  | Intervals |  | Intervals
| Name | Distance | Name | Distance | Name | Distance | Name | Distance |  |  |  | Compress Other Points
1 | M1-1 | 27.75 | i-1 | 1 |  |  | dM1y | 18 |  | 1 | 1 | dM1y | 18
2 | M1-2 | 83.25 | i-2 | 2 |  |  | dremx | 33.75 |  | 1 | 2 | dremx | 33.75
3 | M1-3 | 138.75 | i-3 | 3 |  |  | dremy | 24 |  | 1 | 3 | dremy | 24
4 | M1-4 | 194.25 | i-4 | 4
5 |  |  | i-5 | 5
6 |  |  | i-6 | 6
7 |  |  | i-7 | 7
8 |  |  | i-8 | 8
9 |  |  | i-9 | 9
10 |  |  | i-10 | 10
11 |  |  | i-11 | 11
12 |  |  | i-12 | 12
13
14
15
16
17
18
19
20
Mintervals | 12 | Lintervals | 0 | OtherPoints | 3 | AllPoints | 19 |  | Sorts are done to the 10000th of an inch
Point Lists |  |  |  |  | (run,type,point) | Assending |  |  |  |  | Decending
Point # | Run | Run Point | Name | Distance | GroupID | Dist/Run | Sort | Name | Distance | AssendID | Dist/Run | Sort | Name | Distance | DecendID | LookupID
1 | 1 | 1 | M1-1 | 27.75 | 1101 | 1002775001101 | 1000100001201 | i-1 | 1 | 10001 | 3002775001101 | 3019425001104 | M1-4 | 194.25 | 9805.75 | 10001
2 | 1 | 2 | M1-2 | 83.25 | 1102 | 1008325001102 | 1000200001202 | i-2 | 2 | 10002 | 3008325001102 | 3013875001103 | M1-3 | 138.75 | 9861.25 | 10002
3 | 1 | 3 | M1-3 | 138.75 | 1103 | 1013875001103 | 1000300001203 | i-3 | 3 | 10003 | 3013875001103 | 3008325001102 | M1-2 | 83.25 | 9916.75 | 10003
4 | 1 | 4 | M1-4 | 194.25 | 1104 | 1019425001104 | 1000400001204 | i-4 | 4 | 10004 | 3019425001104 | 3003375001302 | dremx | 33.75 | 9966.25 | 10004
5 | 1 | 5 | i-1 | 1 | 1201 | 1000100001201 | 1000500001205 | i-5 | 5 | 10005 | 3000100001201 | 3002775001101 | M1-1 | 27.75 | 9972.25 | 10005
6 | 1 | 6 | i-2 | 2 | 1202 | 1000200001202 | 1000600001206 | i-6 | 6 | 10006 | 3000200001202 | 3002400001303 | dremy | 24 | 9976 | 10006
7 | 1 | 7 | i-3 | 3 | 1203 | 1000300001203 | 1000700001207 | i-7 | 7 | 10007 | 3000300001203 | 3001800001301 | dM1y | 18 | 9982 | 10007
8 | 1 | 8 | i-4 | 4 | 1204 | 1000400001204 | 1000800001208 | i-8 | 8 | 10008 | 3000400001204 | 3001200001212 | i-12 | 12 | 9988 | 10008
9 | 1 | 9 | i-5 | 5 | 1205 | 1000500001205 | 1000900001209 | i-9 | 9 | 10009 | 3000500001205 | 3001100001211 | i-11 | 11 | 9989 | 10009
10 | 1 | 10 | i-6 | 6 | 1206 | 1000600001206 | 1001000001210 | i-10 | 10 | 10010 | 3000600001206 | 3001000001210 | i-10 | 10 | 9990 | 10010
11 | 1 | 11 | i-7 | 7 | 1207 | 1000700001207 | 1001100001211 | i-11 | 11 | 10011 | 3000700001207 | 3000900001209 | i-9 | 9 | 9991 | 10011
12 | 1 | 12 | i-8 | 8 | 1208 | 1000800001208 | 1001200001212 | i-12 | 12 | 10012 | 3000800001208 | 3000800001208 | i-8 | 8 | 9992 | 10012
13 | 1 | 13 | i-9 | 9 | 1209 | 1000900001209 | 1001800001301 | dM1y | 18 | 10018 | 3000900001209 | 3000700001207 | i-7 | 7 | 9993 | 10018
14 | 1 | 14 | i-10 | 10 | 1210 | 1001000001210 | 1002400001303 | dremy | 24 | 10024 | 3001000001210 | 3000600001206 | i-6 | 6 | 9994 | 10024
15 | 1 | 15 | i-11 | 11 | 1211 | 1001100001211 | 1002775001101 | M1-1 | 27.75 | 10027.75 | 3001100001211 | 3000500001205 | i-5 | 5 | 9995 | 10027.75
16 | 1 | 16 | i-12 | 12 | 1212 | 1001200001212 | 1003375001302 | dremx | 33.75 | 10033.75 | 3001200001212 | 3000400001204 | i-4 | 4 | 9996 | 10033.75
17 | 1 | 17 | dM1y | 18 | 1301 | 1001800001301 | 1008325001102 | M1-2 | 83.25 | 10083.25 | 3001800001301 | 3000300001203 | i-3 | 3 | 9997 | 10083.25
18 | 1 | 18 | dremx | 33.75 | 1302 | 1003375001302 | 1013875001103 | M1-3 | 138.75 | 10138.75 | 3003375001302 | 3000200001202 | i-2 | 2 | 9998 | 10138.75
19 | 1 | 19 | dremy | 24 | 1303 | 1002400001303 | 1019425001104 | M1-4 | 194.25 | 10194.25 | 3002400001303 | 3000100001201 | i-1 | 1 | 9999 | 10194.25
20 | 2 | 1 | M1-1 | 27.75 | 2101 | 2002775002101 | 2000100002201 | i-1 | 1 | 20001 | 2002775002101 | 2019425002104 | M1-4 | 194.25 | 19805.75 | 20001
21 | 2 | 2 | M1-2 | 83.25 | 2102 | 2008325002102 | 2000200002202 | i-2 | 2 | 20002 | 2008325002102 | 2013875002103 | M1-3 | 138.75 | 19861.25 | 20002
22 | 2 | 3 | M1-3 | 138.75 | 2103 | 2013875002103 | 2000300002203 | i-3 | 3 | 20003 | 2013875002103 | 2008325002102 | M1-2 | 83.25 | 19916.75 | 20003
23 | 2 | 4 | M1-4 | 194.25 | 2104 | 2019425002104 | 2000400002204 | i-4 | 4 | 20004 | 2019425002104 | 2003375002302 | dremx | 33.75 | 19966.25 | 20004
24 | 2 | 5 | i-1 | 1 | 2201 | 2000100002201 | 2000500002205 | i-5 | 5 | 20005 | 2000100002201 | 2002775002101 | M1-1 | 27.75 | 19972.25 | 20005
25 | 2 | 6 | i-2 | 2 | 2202 | 2000200002202 | 2000600002206 | i-6 | 6 | 20006 | 2000200002202 | 2002400002303 | dremy | 24 | 19976 | 20006
26 | 2 | 7 | i-3 | 3 | 2203 | 2000300002203 | 2000700002207 | i-7 | 7 | 20007 | 2000300002203 | 2001800002301 | dM1y | 18 | 19982 | 20007
27 | 2 | 8 | i-4 | 4 | 2204 | 2000400002204 | 2000800002208 | i-8 | 8 | 20008 | 2000400002204 | 2001200002212 | i-12 | 12 | 19988 | 20008
28 | 2 | 9 | i-5 | 5 | 2205 | 2000500002205 | 2000900002209 | i-9 | 9 | 20009 | 2000500002205 | 2001100002211 | i-11 | 11 | 19989 | 20009
29 | 2 | 10 | i-6 | 6 | 2206 | 2000600002206 | 2001000002210 | i-10 | 10 | 20010 | 2000600002206 | 2001000002210 | i-10 | 10 | 19990 | 20010
30 | 2 | 11 | i-7 | 7 | 2207 | 2000700002207 | 2001100002211 | i-11 | 11 | 20011 | 2000700002207 | 2000900002209 | i-9 | 9 | 19991 | 20011
31 | 2 | 12 | i-8 | 8 | 2208 | 2000800002208 | 2001200002212 | i-12 | 12 | 20012 | 2000800002208 | 2000800002208 | i-8 | 8 | 19992 | 20012
32 | 2 | 13 | i-9 | 9 | 2209 | 2000900002209 | 2001800002301 | dM1y | 18 | 20018 | 2000900002209 | 2000700002207 | i-7 | 7 | 19993 | 20018
33 | 2 | 14 | i-10 | 10 | 2210 | 2001000002210 | 2002400002303 | dremy | 24 | 20024 | 2001000002210 | 2000600002206 | i-6 | 6 | 19994 | 20024
34 | 2 | 15 | i-11 | 11 | 2211 | 2001100002211 | 2002775002101 | M1-1 | 27.75 | 20027.75 | 2001100002211 | 2000500002205 | i-5 | 5 | 19995 | 20027.75
35 | 2 | 16 | i-12 | 12 | 2212 | 2001200002212 | 2003375002302 | dremx | 33.75 | 20033.75 | 2001200002212 | 2000400002204 | i-4 | 4 | 19996 | 20033.75
36 | 2 | 17 | dM1y | 18 | 2301 | 2001800002301 | 2008325002102 | M1-2 | 83.25 | 20083.25 | 2001800002301 | 2000300002203 | i-3 | 3 | 19997 | 20083.25
37 | 2 | 18 | dremx | 33.75 | 2302 | 2003375002302 | 2013875002103 | M1-3 | 138.75 | 20138.75 | 2003375002302 | 2000200002202 | i-2 | 2 | 19998 | 20138.75
38 | 2 | 19 | dremy | 24 | 2303 | 2002400002303 | 2019425002104 | M1-4 | 194.25 | 20194.25 | 2002400002303 | 2000100002201 | i-1 | 1 | 19999 | 20194.25
39 | 3 | 1 | M1-1 | 27.75 | 3101 | 3002775003101 | 3000100003201 | i-1 | 1 | 30001 | 1002775003101 | 1019425003104 | M1-4 | 194.25 | 29805.75 | 30001
40 | 3 | 2 | M1-2 | 83.25 | 3102 | 3008325003102 | 3000200003202 | i-2 | 2 | 30002 | 1008325003102 | 1013875003103 | M1-3 | 138.75 | 29861.25 | 30002
41 | 3 | 3 | M1-3 | 138.75 | 3103 | 3013875003103 | 3000300003203 | i-3 | 3 | 30003 | 1013875003103 | 1008325003102 | M1-2 | 83.25 | 29916.75 | 30003
42 | 3 | 4 | M1-4 | 194.25 | 3104 | 3019425003104 | 3000400003204 | i-4 | 4 | 30004 | 1019425003104 | 1003375003302 | dremx | 33.75 | 29966.25 | 30004
43 | 3 | 5 | i-1 | 1 | 3201 | 3000100003201 | 3000500003205 | i-5 | 5 | 30005 | 1000100003201 | 1002775003101 | M1-1 | 27.75 | 29972.25 | 30005
44 | 3 | 6 | i-2 | 2 | 3202 | 3000200003202 | 3000600003206 | i-6 | 6 | 30006 | 1000200003202 | 1002400003303 | dremy | 24 | 29976 | 30006
45 | 3 | 7 | i-3 | 3 | 3203 | 3000300003203 | 3000700003207 | i-7 | 7 | 30007 | 1000300003203 | 1001800003301 | dM1y | 18 | 29982 | 30007
46 | 3 | 8 | i-4 | 4 | 3204 | 3000400003204 | 3000800003208 | i-8 | 8 | 30008 | 1000400003204 | 1001200003212 | i-12 | 12 | 29988 | 30008
47 | 3 | 9 | i-5 | 5 | 3205 | 3000500003205 | 3000900003209 | i-9 | 9 | 30009 | 1000500003205 | 1001100003211 | i-11 | 11 | 29989 | 30009
48 | 3 | 10 | i-6 | 6 | 3206 | 3000600003206 | 3001000003210 | i-10 | 10 | 30010 | 1000600003206 | 1001000003210 | i-10 | 10 | 29990 | 30010
49 | 3 | 11 | i-7 | 7 | 3207 | 3000700003207 | 3001100003211 | i-11 | 11 | 30011 | 1000700003207 | 1000900003209 | i-9 | 9 | 29991 | 30011
50 | 3 | 12 | i-8 | 8 | 3208 | 3000800003208 | 3001200003212 | i-12 | 12 | 30012 | 1000800003208 | 1000800003208 | i-8 | 8 | 29992 | 30012
51 | 3 | 13 | i-9 | 9 | 3209 | 3000900003209 | 3001800003301 | dM1y | 18 | 30018 | 1000900003209 | 1000700003207 | i-7 | 7 | 29993 | 30018
52 | 3 | 14 | i-10 | 10 | 3210 | 3001000003210 | 3002400003303 | dremy | 24 | 30024 | 1001000003210 | 1000600003206 | i-6 | 6 | 29994 | 30024
53 | 3 | 15 | i-11 | 11 | 3211 | 3001100003211 | 3002775003101 | M1-1 | 27.75 | 30027.75 | 1001100003211 | 1000500003205 | i-5 | 5 | 29995 | 30027.75
54 | 3 | 16 | i-12 | 12 | 3212 | 3001200003212 | 3003375003302 | dremx | 33.75 | 30033.75 | 1001200003212 | 1000400003204 | i-4 | 4 | 29996 | 30033.75
55 | 3 | 17 | dM1y | 18 | 3301 | 3001800003301 | 3008325003102 | M1-2 | 83.25 | 30083.25 | 1001800003301 | 1000300003203 | i-3 | 3 | 29997 | 30083.25
56 | 3 | 18 | dremx | 33.75 | 3302 | 3003375003302 | 3013875003103 | M1-3 | 138.75 | 30138.75 | 1003375003302 | 1000200003202 | i-2 | 2 | 29998 | 30138.75
57 | 3 | 19 | dremy | 24 | 3303 | 3002400003303 | 3019425003104 | M1-4 | 194.25 | 30194.25 | 1002400003303 | 1000100003201 | i-1 | 1 | 29999 | 30194.25
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112

## DATA
| Point | Distance | Port | Port | Port | Port
| ID | (inches) | A | B | C | D
Run 1 | i-1 | 1 | 66.42 | 93.89 | 112.96 | 77.94
| i-2 | 2 | 74.9 | 119.96 | 128.01 | 85.33
| i-3 | 3 | 82.24 | 127.31 | 136.01 | 89.77
| i-4 | 4 | 87.83 | 129.83 | 138.79 | 97.35
| i-5 | 5 | 92.62 | 135.03 | 143.88 | 104.06
| i-6 | 6 | 96.82 | 137.03 | 145.06 | 106.05
| i-7 | 7 | 100.24 | 141.52 | 148.69 | 109.11
| i-8 | 8 | 102.11 | 140.63 | 149.16 | 111.97
| i-9 | 9 | 104.12 | 145.17 | 152.08 | 113.05
| i-10 | 10 | 105.05 | 145.51 | 152.6 | 114.57
| i-11 | 11 | 108.02 | 149.44 | 156.84 | 116.49
| i-12 | 12 | 108.19 | 148.13 | 154.32 | 117.58
| dM1y | 18 | 115.78 | 155.61 | 162.92 | 126.15
| dremy | 24 | 119.32 | 159.04 | 162.5 | 134.14
| M1-1 | 27.75 | 123.26 | 161.67 | 168.21 | 133.13
| dremx | 33.75 | 129.36 | 161.48 | 168.1 | 139.62
| M1-2 | 83.25 | 162.36 | 159.05 | 160.75 | 168.69
| M1-3 | 138.75 | 161.8 | 156.72 | 172.84 | 176.43
| M1-4 | 194.25 | 147.65 | 161.35 | 165.8 | 143.68
Run 2 | i-1 | 1 | 66.14 | 94.03 | 114.77 | 78.8
| i-2 | 2 | 73.19 | 119.16 | 126.36 | 86.71
| i-3 | 3 | 80.98 | 127.41 | 133.6 | 94.03
| i-4 | 4 | 89.04 | 133.1 | 141.71 | 99.3
| i-5 | 5 | 93.21 | 136.62 | 144.84 | 103.03
| i-6 | 6 | 98.43 | 138.86 | 147.52 | 109.78
| i-7 | 7 | 100.52 | 141.37 | 150.61 | 114.38
| i-8 | 8 | 103.65 | 143.06 | 151.61 | 113.81
| i-9 | 9 | 103.48 | 144.3 | 152.66 | 115.01
| i-10 | 10 | 106.63 | 147.61 | 155.03 | 115.87
| i-11 | 11 | 107.35 | 150.71 | 158.53 | 118.13
| i-12 | 12 | 109.1 | 153.11 | 159.2 | 119.34
| dM1y | 18 | 118.26 | 158.74 | 165.12 | 128.78
| dremy | 24 | 121.08 | 162.15 | 167.55 | 136.44
| M1-1 | 27.75 | 123.28 | 163.83 | 170.2 | 135.09
| dremx | 33.75 | 131.85 | 164.21 | 171.55 | 142.04
| M1-2 | 83.25 | 164.12 | 160.95 | 162.27 | 171.25
| M1-3 | 138.75 | 162.25 | 158.47 | 175.59 | 178.94
| M1-4 | 194.25 | 147.65 | 161.35 | 165.8 | 143.68
Run 3 | i-1 | 1 | 67.23 | 95.16 | 114.95 | 76.9
| i-2 | 2 | 74.45 | 121.61 | 130.06 | 84.87
| i-3 | 3 | 81.95 | 130.42 | 136.89 | 91.48
| i-4 | 4 | 89.26 | 133.86 | 142.58 | 98.51
| i-5 | 5 | 93.86 | 136.93 | 145.22 | 102.6
| i-6 | 6 | 97.66 | 140.15 | 148.54 | 108.11
| i-7 | 7 | 100.08 | 141.87 | 149.4 | 111.89
| i-8 | 8 | 103.9 | 143.75 | 152.58 | 115.94
| i-9 | 9 | 104.88 | 146.66 | 154.57 | 119.26
| i-10 | 10 | 105.89 | 149.78 | 157.94 | 117.52
| i-11 | 11 | 109.39 | 153 | 159.54 | 116.87
| i-12 | 12 | 110.9 | 154.21 | 162.35 | 118.91
| dM1y | 18 | 118.73 | 161.82 | 167.37 | 129.26
| dremy | 24 | 123.29 | 163.28 | 169.94 | 135.25
| M1-1 | 27.75 | 125.72 | 166.39 | 172.51 | 134.56
| dremx | 33.75 | 133.53 | 166.7 | 173.93 | 141.71
| M1-2 | 83.25 | 165.74 | 162.35 | 163.92 | 171.17
| M1-3 | 138.75 | 163.9 | 159.01 | 176.9 | 180.77
| M1-4 | 194.25 | 147.65 | 161.35 | 165.8 | 143.68

## WAF-1
| Point | Distance | Port | Port | Port | Port | LookupID |  | WAF Adjusted Velocities
| ID | (inches) | A | B | C | D |  | Port/Point | 1 | 2 | 3 | 4
Run 1 | M1-1 | 27.75 | 123.26 | 161.67 | 168.21 | 133.13 | 10027.75 | 1 | 109.9345 | 156.6356 | 162.9719 | 118.7375
| M1-2 | 83.25 | 162.36 | 159.05 | 160.75 | 168.69 | 10083.25 | 2 | 154.8703 | 159.05 | 160.75 | 160.9083
| M1-3 | 138.75 | 161.8 | 156.72 | 172.84 | 176.43 | 10138.75 | 3 | 154.3361 | 156.72 | 172.84 | 168.2912
| M1-4 | 194.25 | 147.65 | 161.35 | 165.8 | 143.68 | 10194.25 | 4 | 131.6877 | 156.3255 | 160.637 | 128.1469
ash corner flow interval sumation
Corner Interval Flow Sumations
| i-0 | 0 | 0 | 0 | 0 | 0 |  |  | A | B | C | D |  | A | B | C | D
| i-1 | 1 | 66.42 | 93.89 | 112.96 | 77.94 | 10001 |  | 3005.505 | 4248.5225 | 5111.44 | 3526.785 |  | 3005.505 | 4248.5225 | 5111.44 | 3526.785
| i-2 | 2 | 74.9 | 119.96 | 128.01 | 85.33 | 10002 |  | 6253.41 | 9462.8625 | 10662.9225 | 7224.6975 |  | 6253.41 | 9462.8625 | 10662.9225 | 7224.6975
| i-3 | 3 | 82.24 | 127.31 | 136.01 | 89.77 | 10003 |  | 6796.305 | 10694.4275 | 11418.865 | 7573.075 |  | 6796.305 | 10694.4275 | 11418.865 | 7573.075
| i-4 | 4 | 87.83 | 129.83 | 138.79 | 97.35 | 10004 |  | 7185.4575 | 10864.165 | 11610.3 | 7905.82 |  | 7185.4575 | 10864.165 | 11610.3 | 7905.82
| i-5 | 5 | 92.62 | 135.03 | 143.88 | 104.06 | 10005 |  | 7443.5625 | 10925.475 | 11660.1375 | 8308.1625 |  | 7443.5625 | 10925.475 | 11660.1375 | 8308.1625
| i-6 | 6 | 96.82 | 137.03 | 145.06 | 106.05 | 10006 |  | 7624.96 | 10950.415 | 11629.835 | 8456.9275 |  | 7624.96 | 10950.415 | 11629.835 | 8456.9275
| i-7 | 7 | 100.24 | 141.52 | 148.69 | 109.11 | 10007 |  | 7734.605 | 10933.0875 | 11529.6875 | 8445.03 |  | 7734.605 | 10933.0875 | 11529.6875 | 8445.03
| i-8 | 8 | 102.11 | 140.63 | 149.16 | 111.97 | 10008 |  | 7739.8875 | 10792.2375 | 11392.7625 | 8456.31 |  | 7739.8875 | 10792.2375 | 11392.7625 | 8456.31
| i-9 | 9 | 104.12 | 145.17 | 152.08 | 113.05 | 10009 |  | 7682.0675 | 10646.05 | 11221.19 | 8381.995 |  | 7682.0675 | 10646.05 | 11221.19 | 8381.995
| i-10 | 10 | 105.05 | 145.51 | 152.6 | 114.57 | 10010 |  | 7582.4125 | 10537.15 | 11044.65 | 8251.225 |  | 7582.4125 | 10537.15 | 11044.65 | 8251.225
| i-11 | 11 | 108.02 | 149.44 | 156.84 | 116.49 | 10011 |  | 7510.7175 | 10396.9875 | 10907.76 | 8144.865 |  | 7510.7175 | 10396.9875 | 10907.76 | 8144.865
| i-12 | 12 | 108.19 | 148.13 | 154.32 | 117.58 | 10012 |  | 7405.1925 | 10191.7725 | 10657.23 | 8016.8975 |  | 7405.1925 | 10191.7725 | 10657.23 | 8016.8975
| dM1y | 18 | 115.78 | 155.61 | 162.92 | 126.15 | 10018 | sum | 83964.0825 | 120643.1525 | 128846.78 | 92691.79 | sum | 83964.0825 | 120643.1525 | 128846.78 | 92691.79
| dremx | 33.75 | 129.36 | 161.48 | 168.1 | 139.62 | 10033.75
| dremy | 24 | 119.32 | 159.04 | 162.5 | 134.14 | 10024
| Vc | -- | 123.26 | 155.61 | 162.92 | 133.13
| Vdremc | -- | 129.36 | 159.04 | 162.5 | 139.62
| ^vx |  | 120.75 | 154.3021 | 161.3259 | 130.7739
| ^vy |  | 109.3929 | 148.7874 | 153.9233 | 122.3289
| ^vc |  | 109.6176 | 143.4839 | 149.3978 | 119.3469
Average
| Cx | 0.96886 | 0.97964 | 0.95443 | 0.95907 | 0.9823
| Cy | 0.95387 | 0.94483 | 0.95616 | 0.94478 | 0.96971
| C*c | 0.90622 | 0.88932 | 0.92207 | 0.917 | 0.89647
| Cc | 0.89189 | 0.87526 | 0.9075 | 0.90251 | 0.8823
| Vunadj | 157.7119
| Vadj | 150.8027
| WAF | 0.95619
| Roughness | 0.028178 | 0.052274 | 0.036835 | 0.0030686 | 0.020533
| b/a | 0.64865
| fRe | 59.6332
| Dh | 14.5574
| Deff | 15.6234
| Ccadj | 0.98419

## WAF-2
| Point | Distance | Port | Port | Port | Port | LookupID |  | WAF Adjusted Velocities
| ID | (inches) | A | B | C | D |  | Port/Point | 1 | 2 | 3 | 4
Run 2 | M1-1 | 27.75 | 123.28 | 163.83 | 170.2 | 135.09 | 20027.75 | 1 | 110.2973 | 159.848 | 166.0632 | 120.8636
| M1-2 | 83.25 | 164.12 | 160.95 | 162.27 | 171.25 | 20083.25 | 2 | 156.3443 | 160.95 | 162.27 | 163.1365
| M1-3 | 138.75 | 162.25 | 158.47 | 175.59 | 178.94 | 20138.75 | 3 | 154.5629 | 158.47 | 175.59 | 170.4622
| M1-4 | 194.25 | 147.65 | 161.35 | 165.8 | 143.68 | 20194.25 | 4 | 132.1009 | 157.4283 | 161.7701 | 128.549
ash corner flow interval sumation
Corner Interval Flow Sumations
| i-0 | 0 | 0 | 0 | 0 | 0 |  |  | A | B | C | D |  | A | B | C | D
| i-1 | 1 | 66.14 | 94.03 | 114.77 | 78.8 | 20001 |  | 2992.835 | 4254.8575 | 5193.3425 | 3565.7 |  | 2992.835 | 4254.8575 | 5193.3425 | 3565.7
| i-2 | 2 | 73.19 | 119.16 | 126.36 | 86.71 | 20002 |  | 6165.3525 | 9433.6575 | 10670.0025 | 7323.8175 |  | 6165.3525 | 9433.6575 | 10670.0025 | 7323.8175
| i-3 | 3 | 80.98 | 127.41 | 133.6 | 94.03 | 20003 |  | 6667.8525 | 10664.1525 | 11243.27 | 7817.005 |  | 6667.8525 | 10664.1525 | 11243.27 | 7817.005
| i-4 | 4 | 89.04 | 133.1 | 141.71 | 99.3 | 20004 |  | 7183.345 | 11006.5475 | 11631.8475 | 8168.1925 |  | 7183.345 | 11006.5475 | 11631.8475 | 8168.1925
| i-5 | 5 | 93.21 | 136.62 | 144.84 | 103.03 | 20005 |  | 7517.8125 | 11125.95 | 11820.1875 | 8346.1125 |  | 7517.8125 | 11125.95 | 11820.1875 | 8346.1125
| i-6 | 6 | 98.43 | 138.86 | 147.52 | 109.78 | 20006 |  | 7713.51 | 11088.07 | 11767.49 | 8565.6025 |  | 7713.51 | 11088.07 | 11767.49 | 8565.6025
| i-7 | 7 | 100.52 | 141.37 | 150.61 | 114.38 | 20007 |  | 7808.7875 | 10999.0275 | 11701.6025 | 8798.28 |  | 7808.7875 | 10999.0275 | 11701.6025 | 8798.28
| i-8 | 8 | 103.65 | 143.06 | 151.61 | 113.81 | 20008 |  | 7809.5025 | 10879.4475 | 11559.915 | 8728.2675 |  | 7809.5025 | 10879.4475 | 11559.915 | 8728.2675
| i-9 | 9 | 103.48 | 144.3 | 152.66 | 115.01 | 20009 |  | 7715.5925 | 10704.16 | 11334.0575 | 8523.545 |  | 7715.5925 | 10704.16 | 11334.0575 | 8523.545
| i-10 | 10 | 106.63 | 147.61 | 155.03 | 115.87 | 20010 |  | 7616.4875 | 10581.7375 | 11153.7625 | 8369.4 |  | 7616.4875 | 10581.7375 | 11153.7625 | 8369.4
| i-11 | 11 | 107.35 | 150.71 | 158.53 | 118.13 | 20011 |  | 7542.795 | 10515.78 | 11052.99 | 8248.5 |  | 7542.795 | 10515.78 | 11052.99 | 8248.5
| i-12 | 12 | 109.1 | 153.11 | 159.2 | 119.34 | 20012 |  | 7413.4125 | 10405.835 | 10882.2525 | 8133.3475 |  | 7413.4125 | 10405.835 | 10882.2525 | 8133.3475
| dM1y | 18 | 118.26 | 158.74 | 165.12 | 128.78 | 20018 | sum | 84147.285 | 121659.2225 | 130010.72 | 94587.77 | sum | 84147.285 | 121659.2225 | 130010.72 | 94587.77
| dremx | 33.75 | 131.85 | 164.21 | 171.55 | 142.04 | 20033.75
| dremy | 24 | 121.08 | 162.15 | 167.55 | 136.44 | 20024
| Vc | -- | 123.28 | 158.74 | 165.12 | 135.09
| Vdremc | -- | 131.85 | 162.15 | 167.55 | 142.04
| ^vx |  | 122.7504 | 156.6832 | 164.3111 | 133.1038
| ^vy |  | 110.6414 | 151.2329 | 157.7233 | 124.53
| ^vc |  | 111.0104 | 145.6175 | 152.6191 | 121.5603
Average
| Cx | 0.97569 | 0.9957 | 0.95638 | 0.9654 | 0.9853
| Cy | 0.95262 | 0.93558 | 0.95271 | 0.9552 | 0.967
| C*c | 0.91049 | 0.90047 | 0.91733 | 0.92429 | 0.89985
| Cc | 0.89469 | 0.88485 | 0.90142 | 0.90826 | 0.88423
| Vunadj | 159.045
| Vadj | 152.4192
| WAF | 0.95834
| Roughness | 0.034376 | 0.059273 | 0.052088 | 0.0044323 | 0.02171
| b/a | 0.64865
| fRe | 59.6332
| Dh | 14.5574
| Deff | 15.6234
| Ccadj | 0.98265

## WAF-3
| Point | Distance | Port | Port | Port | Port | LookupID |  | WAF Adjusted Velocities
| ID | (inches) | A | B | C | D |  | Port/Point | 1 | 2 | 3 | 4
Run 3 | M1-1 | 27.75 | 125.72 | 166.39 | 172.51 | 134.56 | 30027.75 | 1 | 111.8625 | 162.0102 | 167.9691 | 119.7282
| M1-2 | 83.25 | 165.74 | 162.35 | 163.92 | 171.17 | 30083.25 | 2 | 157.4085 | 162.35 | 163.92 | 162.5656
| M1-3 | 138.75 | 163.9 | 159.01 | 176.9 | 180.77 | 30138.75 | 3 | 155.661 | 159.01 | 176.9 | 171.683
| M1-4 | 194.25 | 147.65 | 161.35 | 165.8 | 143.68 | 30194.25 | 4 | 131.3753 | 157.1029 | 161.4358 | 127.8429
ash corner flow interval sumation
Corner Interval Flow Sumations
| i-0 | 0 | 0 | 0 | 0 | 0 |  |  | A | B | C | D |  | A | B | C | D
| i-1 | 1 | 67.23 | 95.16 | 114.95 | 76.9 | 30001 |  | 3042.1575 | 4305.99 | 5201.4875 | 3479.725 |  | 3042.1575 | 4305.99 | 5201.4875 | 3479.725
| i-2 | 2 | 74.45 | 121.61 | 130.06 | 84.87 | 30002 |  | 6269.34 | 9592.0725 | 10841.6925 | 7158.3225 |  | 6269.34 | 9592.0725 | 10841.6925 | 7158.3225
| i-3 | 3 | 81.95 | 130.42 | 136.89 | 91.48 | 30003 |  | 6764.3 | 10900.2975 | 11545.5875 | 7627.1375 |  | 6764.3 | 10900.2975 | 11545.5875 | 7627.1375
| i-4 | 4 | 89.26 | 133.86 | 142.58 | 98.51 | 30004 |  | 7233.6225 | 11165.83 | 11807.6075 | 8027.0775 |  | 7233.6225 | 11165.83 | 11807.6075 | 8027.0775
| i-5 | 5 | 93.86 | 136.93 | 145.22 | 102.6 | 30005 |  | 7553.7 | 11170.0875 | 11871.75 | 8295.7875 |  | 7553.7 | 11170.0875 | 11871.75 | 8295.7875
| i-6 | 6 | 97.66 | 140.15 | 148.54 | 108.11 | 30006 |  | 7708.68 | 11152.47 | 11823.84 | 8481.0775 |  | 7708.68 | 11152.47 | 11823.84 | 8481.0775
| i-7 | 7 | 100.08 | 141.87 | 149.4 | 111.89 | 30007 |  | 7761.295 | 11069.285 | 11694.145 | 8635 |  | 7761.295 | 11069.285 | 11694.145 | 8635
| i-8 | 8 | 103.9 | 143.75 | 152.58 | 115.94 | 30008 |  | 7802.235 | 10924.965 | 11550.735 | 8714.4975 |  | 7802.235 | 10924.965 | 11550.735 | 8714.4975
| i-9 | 9 | 104.88 | 146.66 | 154.57 | 119.26 | 30009 |  | 7777.055 | 10817.7725 | 11441.3375 | 8761.2 |  | 7777.055 | 10817.7725 | 11441.3375 | 8761.2
| i-10 | 10 | 105.89 | 149.78 | 157.94 | 117.52 | 30010 |  | 7640.4125 | 10745.95 | 11328.4875 | 8583.275 |  | 7640.4125 | 10745.95 | 11328.4875 | 8583.275
| i-11 | 11 | 109.39 | 153 | 159.54 | 116.87 | 30011 |  | 7588.62 | 10672.995 | 11191.17 | 8262.2475 |  | 7588.62 | 10672.995 | 11191.17 | 8262.2475
| i-12 | 12 | 110.9 | 154.21 | 162.35 | 118.91 | 30012 |  | 7544.9325 | 10521.9425 | 11024.7325 | 8075.465 |  | 7544.9325 | 10521.9425 | 11024.7325 | 8075.465
| dM1y | 18 | 118.73 | 161.82 | 167.37 | 129.26 | 30018 | sum | 84686.35 | 123039.6575 | 131322.5725 | 94100.8125 | sum | 84686.35 | 123039.6575 | 131322.5725 | 94100.8125
| dremx | 33.75 | 133.53 | 166.7 | 173.93 | 141.71 | 30033.75
| dremy | 24 | 123.29 | 163.28 | 169.94 | 135.25 | 30024
| Vc | -- | 125.72 | 161.82 | 167.37 | 134.56
| Vdremc | -- | 133.53 | 163.28 | 169.94 | 141.71
| ^vx |  | 124.1902 | 158.9504 | 166.4757 | 132.753
| ^vy |  | 112.3044 | 152.4726 | 159.7779 | 123.5946
| ^vc |  | 112.158 | 146.8989 | 154.5245 | 121.1442
Average
| Cx | 0.97368 | 0.98783 | 0.95529 | 0.96502 | 0.98657
| Cy | 0.94973 | 0.94588 | 0.94224 | 0.95464 | 0.95617
| C*c | 0.90587 | 0.89213 | 0.90779 | 0.92325 | 0.9003
| Cc | 0.88978 | 0.87628 | 0.89167 | 0.90685 | 0.88431
| Vunadj | 160.0888
| Vadj | 153.0516
| WAF | 0.95604
| Roughness | 0.036046 | 0.059284 | 0.04957 | 0.0065646 | 0.028766
| b/a | 0.64865
| fRe | 59.6332
| Dh | 14.5574
| Deff | 15.6234
| Ccadj | 0.98224

## RESULTS
WAF Results Summary
| Run 1 | Run 2 | Run 3 | Average
Average Unadjusted Velocity | 157.7119 | 159.045 | 160.0888 | 158.9485
Average Adjusted Velocity | 150.8027 | 152.4192 | 153.0516 | 152.0911
WAF | 0.95619 | 0.95834 | 0.95604 | 0.95686