NSPS Particulate Testing Requirements (40 CFR 60)

All subparts specify EPA Method 5 unless otherwise specified.

N/S = Not Specified.  In these cases, either process-specific or Method 1-5 requirements would apply.

| Subpart | Facility | Minimum Sample Time (minutes) | Minimum Sample Volume (dscf) | Filter Temperature (°F) | Comments |
| --- | --- | --- | --- | --- | --- |
| D | Fossil-fired boilers | 60 | 30 | 320±25°F | Method 5B required after FGD |
| Da | Electric Utilities | 120 | 60 | 320±25°F | Method 5B required after FGD |
| Db | Industrial Boilers | 120 | 60 | 320 | Method 5B required after FGD Method 17 allowed if gas temperature is less than 320°F. |
| Dc | Small Industrial Boilers | 120 | 60 | 320 | Method 5B required after FGD Method 17 allowed if gas temperature is less than 320°F. |
| Ea | Municipal Waste Combustors, 1989-1994 construction | N/S | 60 | 320±25°F |  |
| Eb | Municipal Waste Combustors, constructed after 1994 | N/S | 60 | 320±25°F | 240 minute test specified for Dioxins |
| Ec | Hospital Incinerators | 60 | N/S | N/S | 240 minute test specified for Dioxins |
| F | Portland Cement Mfg. | 60 | 30 | N/S | 40.6 dscf required for Clinker Cooler |
| N | Basic Oxygen Process, Primary Emissions | 60 | 53 | N/S | Integral # of heats or blows. |
| NA | Basic Oxygen Process, Secondary Emissions | N/S | 200 | N/S | Sampling done only during steel production. |
| O | Sewage Treatment Facilities | 60 | 31.8 | N/S |  |
| P | Primary Copper Smelters | 60 | 30 | N/S |  |
| Q | Primary Zinc Smelters | 60 | 30 | N/S |  |
| R | Primary Lead Smelters | 60 | 30 | N/S |  |
| Y | Coal Preparation Plants | 60 | 30 | N/S | Sampling must begin no less than 30 minutes after startup and end before shutdown procedures commence. |
| Z | Ferro-Alloy Electric Arc Furnaces (EAF) | 60 | 63.6 | N/S | Integral # of furnace cycles. |
| AA | Steel EAF, 1974-1983 construction | 240 | 160 | N/S | Integral # of heats if single furnace. Use Method 5D for Positive Pressure Baghouses. |
| AAa | Steel EAF/AOD, constructed after 1983 | 240 | 160 | N/S | Integral # of heats if single furnace. Use Method 5D for Positive Pressure Baghouses. |
| BB | Kraft Pulp Mills | 60 | 31.8 | N/S | Use water instead of acetone to rinse |
| CC | Glass Mfg. | 60 | 31.8 | 350±25°F | 248±25°F if gas-fired or <0.5%w/w sulfur oil |
| DD | Grain Elevators | 60 | 60 | Ambient | No heaters allowed |
| HH | Lime Mfg. | 60 | 31.8 | N/S | 5D for positive pressure baghouses |
| LL | Metallic Mineral Processing | N/S | 60 | <250 | Method 17 allowed. |
| NN | Phosphate Rock Processing | 60 | 30 | N/S |  |
| PP | Ammonium Sulfate Mfg. | 60 | 53 | N/S |  |
| UU | Asphalt and Asphalt Roofing Materials Mfg. | 120 | 106 | N/S | Method 5A specifies 108±18°F |
| OOO | Non-metallic Mineral Processing | N/S | 60 | <250 | Allows Method 17 |
| PPP | Wool Fiberglass Insulation Mfg. | 120 | 90 | N/S | Method 5E required |
| UUU | Calciners and Dryers in Mineral Processing | 120 | 60 | N/S |  |